| Storage Tanks TECHNICAL GUIDE | TG 13200 |
| --- | --- |

1.	COORDINATION ISSUES:   (Not Used)

2.	DESIGN ISSUES:      (Not Used)

3.	DRAWING NOTES:   (Not Used)

4.	STANDARD DRAWINGS:    (Not Used)

5.	SPECIFICATION NOTES:

5.1	Venting Storage Tanks During Closure:

5.1.1	Problem:  A problem can occur when storage tanks are being removed or closed and the process requires that the tanks be cleaned. Cleaning may be necessary to comply with shipping regulations, when the tank is to be removed, or closure regulations, when the tank is to be abandoned. In order to properly clean the tank, it may need to be ventilated or degassed prior to allowing the cleaning crew to begin work.  Indiscriminate ventings of fumes / vapors to the atmosphere have undesirable consequences when the project is close to an occupied area. This very situation has already resulted in complaints and lost State employee time due to odors migrating to occupied areas.

5.1.2	Solution:  In order to preclude the above situation from recurring, one of the following three general methods shall be specified by the architect or designer:

5.1.2.1	The vented vapors shall be collected and treated by an appropriate scrubber or other method that shall render the gases odorless prior to their release to the atmosphere; or

5.1.2.2	The vapors shall be vented not less than 200 yards from any occupied area (details to accomplish this to be shown on the plans); or

5.1.2.3	The vapors shall be vented according to a time schedule that will insure that any areas within 200 yards of the vapors are not occupied during and for at least one hour after any venting.

5.1.3	Additional Considerations:  The specifications shall include two additional contract requirements:

5.1.3.1	The first shall provide for the stopping of any or all work if odors cause operational problems for occupants of adjacent facilities.

5.1.3.2	The second shall hold the Contractor responsible for related costs if he does not comply with these requirements.

6.	GUIDE SPECIFICATION:    (Not Used)

END OF SECTION 13200