| Fire Protection DESIGN CRITERIA | DC 2.5 |
| --- | --- |

2.5.1	Piping and Equipment:   Do not locate piping and other water containing equipment directly over electrical equipment, panel boxes, controls, switches and other energized electrical devices.  The Electric Code[NEC 1999 110-26 (f)(1)(a)] does not allow placement of piping, equipment and other plumbing hardware over electrical panels, switchboards and other panels under its jurisdiction.  Do not route piping and do not locate fire protection equipment in electric rooms, electric vaults and electric closets.  Designer shall provide coordinated drawings to DAGS prior to final drawings.  Specifications shall require contractor to submit coordination drawings showing all existing conditions and new work.