| Roof Maintenance and Repair TECHNICAL GUIDE | TG 07590 |
| --- | --- |

1.	COORDINATION ISSUES:

1.1	Removal of Asbestos Containing Roofing Materials: Coordinate with the requirements of Technical Guide TG13280 - Hazardous Material Remediation.

2.	DESIGN ISSUES:     (Not Used)

3.	DRAWING NOTES:   (Not Used)

4.	STANDARD DRAWINGS:    (Not Used)

5.	SPECIFICATION NOTES:

5.1	Reroofing Guidelines:  The following guidelines shall govern all Repair & Maintenance reroofing projects done under the DAGS Division of Public Works jurisdiction:

5.1.1	For projects to be implemented when the facility is not occupied:

5.1.1.1	On roofs with inadequate slope to drain (i.e. ponding conditions:

a.	Single-ply roofing membrane system (EPDM)

5.1.1.2	On roofs with marginal slope to drain but no ponding conditions

a.	Modified bitumen membrane system OR

b.	Single-ply roofing membrane system OR

c.	Smooth or mineral-surfaced BUR.  (Use only if required to tie-in to or repair and existing BUR roof.)

5.1.1.3	On roofs with good, complete drainage, use any of the systems listed in 5.1.1.2 above

5.1.2	For projects which may be reroofed when the facility is occupied (bldgs w/ concrete decks):

5.1.2.1	On roofs with more than 1/2" per foot slope, use either torched-on (not hot-mopped) modified bitumen or single-ply membrane system.

5.1.2.2	On roofs with less than 1/2" per foot slope and/or ponding conditions, use a single-ply roofing membrane system.

5.1.3	Other Considerations:

5.1.3.1	Consultant is responsible to field verify the slope of the existing roof deck and to show any ponding conditions on the roof plans.

5.1.3.2	Where the roof slope exceeds 1/2" per foot, the consultant is advised to address installation of the membrane parallel to the roof slope and/or backnailing of the roofing plies to prevent slippage.

5.1.3.3	Where the roof slope is to be built-up to eliminate ponding conditions, the consultant shall also consider the over-all thickness and cost necessary to build-up the slope when selecting the roof membrane (i.e. installation of a single-ply membrane may be more cost effective in lieu of a modified bitumen membrane atop built-up insulation).

5.1.3.4	Provision of built-up gravel roofs and floodcoating of existing gravel roofs is discouraged since it is almost impossible to locate and properly repair leaks.

5.1.3.5	Address mitigating measures where the existing roof membrane has been damaged by vandals.

5.1.4	Use of Asphalt Primer:

5.1.4.1	Problem: DAGS has observed that the original primer (and even a thin layer of asphalt) remains on the deck following a tear-off. New priming of the deck is therefore not essential. Furthermore, since it takes asphalt primer about a half-day to dry, the potential exposure of the deck to rain is heightened unnecessarily.

5.1.4.2	Solution:   Omit the application of asphalt primer when specifying complete tear-off and reroofing of existing concrete decks.

5.2	Metal Roof Coating:

5.2.1	Problem: In the past, the majority of the metal roofs on the Big Island which were field painted were finished using Portland Cement or acrylic paints. However, due to discoloration and fading of the newer paint formulations, they are no longer used or should be specified and have been replaced by acrylic paints.

5.2.2	Recommendations for island of Hawaii:  On repainting projects on the Big Island, follow these roof painting guidelines:

5.2.2.1	Unless the project requires special coatings for corrosion resistance (i.e. aliphatic acrylic polyurethane paints), specify only resin fortified acrylic paints having pigments "ground" into the paint at the factory.

5.2.2.2	Examples of such paints and the colors used which have performed well are as follows:

a.	Benjamin Moore #129 Acrylic Roof Paint (Forest Green)

b.	Sinclair Dectone (Parkway Green)

5.2.2.3	Notes:

a.	The actual field performance of equivalent paints including those submitted for substitution shall be verified by the consultant and approved by the Quality Control Branch DAGS District Manager.

b.	As with other areas, the compatibility between the new and existing paint shall be verified.

5.2.2.4	Paints which have performed poorly or which have exhibited discoloration, fading and/or color shifting shall not be specified. Examples based on past DAGS projects are as follows:

a.	Portland Cement paint

b.	United Coatings Roofshield 60

5.2.3	Recommendations for all other islands:  On repainting projects on Oahu and the other neighbor islands, the same guidelines (with the exception of the selected paint color) shall be applied.

6.	GUIDE SPECIFICATION:  (Not Used)

END OF SECTION 07590