| Interior Lighting TECHNICAL GUIDE | TG 16510 |
| --- | --- |

1.	COORDINATION ISSUES:

1.1	Light Fixture Location: Coordinate electrical drawings with all project architectural and engineering disciplines and resolve all light fixture location conflicts.

2.	DESIGN ISSUES:

2.1	Time Clocks for Night Lights: Do not specify timers with monthly, daylight savings, or year-round scheduling features.  These complicated timers are not user friendly and generate maintenance service calls.  Instead, simple 24-hour timers shall be specified.

2.2	Problem Light Fixtures:

2.2.1	Two-tube, 96" high output fluorescent fixture with metal “egg-crate” diffuser, pendant mounted:

2.2.1.1	Problem: Apparent spontaneous loosening of the mounting nuts at the lower end of pendant stem, resulting in the falling of the fixture.  In one instance, the ball at the top of the pendant stem fell apart.  The exact circumstances leading to this problem, such as inadequate tightening of the mounting nuts at installation, has not been verified.  As this happened in several different installations, however, it would appear that the tendency for the problem to occur with this type of fixture is real.

2.2.1.2	Recommendation: Avoid using this type of fixture unless absolutely necessary.  If unavoidable, insure that loosening of the mounting nuts is prevented by some mechanical means such as flaring the threads or using cotter pins.

2.2.2	Surface Mounted Light Fixture Subject to Vandalism:

2.2.2.1	Problem: In areas where fixtures are reachable (±9'-0" high) and subject to vandalism, surface mounted fixtures can be rotated if installed only by a single stud bolt.  Mounting by stud bolt alone is an acceptable installation procedure and can meet the pullout resistance required by the National Electric Code.  However, mounting by a single stud bolt alone allows the fixture to be rotated.

2.2.2.2	Recommendation: To prevent rotation, fixtures (and housing) should be secured to the substrate in at least two separate mounting locations.  In addition to a single stud bolt, provide another separate mounting location to secure the fixture.  Specify or provide an appropriate detail requiring at least two fastener locations to mount the fixture.

3.	DRAWING NOTES: (Not Used)

4.	STANDARD DRAWINGS: (Not Used)

5.	SPECIFICATION NOTES: (Not Used)

6	GUIDE SPECIFICATION: (Not Used)