| Water Distribution TECHNICAL GUIDE | TG 02510 |
| --- | --- |

1.	COORDINATION ISSUES:  (Not Used)

2.	DESIGN ISSUES:  (Not Used)

3.	DRAWING NOTES:

3.1	Backflow Preventer Detail:

3.1.1	Problem: The maximum 48" installation height permitted in Note 4 of Backflow Preventer Standard Detail No. V9, often referenced in our project specifications creates a problem. (Reference: “Approved Material List and Standard Details for Water System Construction”, State of Hawaii, 2002.)  Vandals have additional leverage to rock the device back and forth, causing leaks at the joints and fittings.

3.1.2	Solution: Details shall show that the device only be installed at the recommended heights (H) noted in the table.

4.	STANDARD DRAWINGS:

4.1	Modified Standard Backflow Preventer Detail:  Where 3/4" to 1-1/2" diameter pipes are used, include a support system to secure pipes.  Refer to the attached modified standard detail. A/TG 02510.

5.	SPECIFICATION NOTES:

5.1	Specification Paragraphs:  The Consultant shall utilize the following specification paragraphs and information as appropriate in the development of the Project Specifications.

6.	GUIDE SPECIFICATION:

6.1	Certificates (Part 1)

6.1.1	Before installation, submit affidavits from the manufacturers or suppliers of pressure water pipe and pipe coating certifying that materials furnished comply with the Contract Documents.

END OF SECTION 0251